	2024 ASBESTOS REGISTER – FLORENCE HOUSE, Rockhampton Girls Grammar School  
Date of register: 06/06/2024
NOTE: A demolition or refurbishment survey should be carried out by a competent person before undertaking refurbishment or demolition work.

	Workplace address:
	Rockhampton Girls 
Grammar School –
Denham Street, 
Rockhampton City QLD 4700
	Name and contact details of competent person:
	Lawrence Lyons
Asbestos Assessor Licence No. 2317266

Environics (QLD) Pty Ltd
ABN 76 354 368 913
Tel. 0429 128 145

	Workplace owner / manager:
	Kasey Mitchell
Facilities and Services Manager Rockhampton Girls Grammar School 
Tel. 0427 414 819

	Areas not assessed:
	Ceiling cavities located beyond inspection openings, utility pits, and elevated areas where safety measures cannot be practically implemented.

	Asbestos related 
documents:
	ENV-2023-062  Ver 1-4 Asbestos Management Plan & ACM Register - RGGS, Denham St The Range Q 4700.pdf   
· Appendix One	ENV-2023-062-RGGS-ASBESTOS REGISTER-v1-02.10.2024. (this document)
· Appendix Two         RGGS-691-PRO-ASBESTOS-MANAGEMENT-PROCEDURE-v1-24.07.2024
· Appendix Three      RGGS-692-PRO-ASBESTOS-INCIDENT-MANAGEMENT-PROCEDURE-v1-24.07.2024
· Appendix Four       RGGS-720-GDL-ASBESTOS-MANAGEMENT-POSTER-v1-24.07.2024


	Consultation:
	Attach minutes of relevant future meeting to this document.

	Disclaimer and 
Limitations:
	Inspections were limited to accessible areas without dismantling or removing objects, including vegetation, insulation, coverings, furnishings, and personal belongings. Areas such as inside walls, between floors, and behind stored items were not inspected. No destructive procedures were performed, and relevant legislation was followed. For further details on regulations, please refer to additional materials. Compliance and Liability: This register does not serve as a 'Certificate of Compliance' unless specified and does not warranty against future asbestos issues. The report does not confirm that all areas are asbestos-free. The competent person is not liable for undetectable asbestos requiring structural disruption. 

	

Date
	
Sample       No.
	Type of material identified or assumed and amount 
(Cross-sectional areas
 are estimates – measure before quoting)
	
Friable or non-friable asbestos
	

Condition of asbestos
	
Specific location of identified or assumed asbestos
	


Notes

	06/06/2024

	
GF-F3-8
	
Chrysotile & Amosite Asbestos 
10m2
	

Friable
	
Painted & in good condition
	
Interior:
North wall behind shower/toilets
closest to hall
	
19 October 2013 SLR report:
North wall behind shower/toilets closest to hall - Chrysotile & Amosite Asbestos detected - LOW DENSITY BOARD. Sample GF-F3-8. (Photo 270, 10m2)

	06/06/2024

	
GF-F3-9
	
Chrysotile Asbestos 
2m2
	

Non-friable
	
Painted & in good condition
	
Interior:
North wall behind shower/toilets
closest to hall
	
19 October 2013 SLR report:
Upper east wall behind shower/toilets closest to hall - Chrysotile Asbestos detected. Sample GF-F3-9. (Photo 271, 2m2)

	06/06/2024

	GF-F2
	
Chrysotile Asbestos 
2m2
	

Non-friable
	
Painted & in good condition
	
Interior:
North wall behind shower/toilets
closest to hall
	
19 October 2013 SLR report:
Internal wall sheeting to the Laundry - Chrysotile Asbestos fibre detected.
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Date
	
Sample       No.
	Type of material identified or assumed and amount 
(Cross-sectional areas
 are estimates – measure before quoting)
	
Friable or non-friable asbestos
	

Condition of asbestos
	
Specific location of identified or assumed asbestos
	


Notes

	06/06/2024

	
GF-F1
	
Chrysotile Asbestos 
3 m2
	
Non-friable unless removed using an abrasive method of removal i.e. lift & grinding concrete

	
Fair condition
	
Interior:
Vinyl tiles to the Laundry floor
	
19 October 2013 SLR report:
Vinyl tiles to the Laundry floor – 
Chrysotile Asbestos fibre detected.

	06/06/2024

	
GF-F3-11
	
Chrysotile & Amosite Asbestos 
9 m2
	

Confirm type using pentation test following removal of Tilux cover sheet before quoting to remove (amosite present)
	
Good condition
	
Interior:
South wall behind Tilux sheeting
	
19 October 2013 SLR report:
South wall behind Tilux sheeting - Chrysotile & Amosite Asbestos detected. Sample GF-F3-11. (Photo 272, 9m2).

	06/06/2024

	GF-F3-12
	
Chrysotile Asbestos 
8 m2
	

Non-friable
	
Good condition
	
Interior:
Bathroom
	
19 October 2013 SLR report:
Tilux sheeting throughout bathroom - Chrysotile Asbestos detected. Sample GF-F3-12. (Photo 273, 8m2).

	06/06/2024

	-
	-
	
See SLR notes
	-
	Interior:
West wall (dividing wall between 2 sections of bathroom)
	19 October 2013 SLR report:
West wall (dividing wall between 2 sections of bathroom) is presumed - material is too hard to sample).

	06/06/2024

	GF-F4-4
	Chrysotile & Amosite Asbestos 
1 m2
	
Non-friable
	
Good condition
	Interior:
Skylight in main house bathroom
	19 October 2013 SLR report:
Skylight in main house bathroom - - Chrysotile Asbestos detected. Sample GF-F4-4 (1m2).

	06/06/2024

	GF-F4-2
	Chrysotile & Amosite Asbestos 
3 m2
	Confirm type using pentation test before quoting to remove (amosite present)
	
Good condition
	Interior:
Ceiling to side entrance to main house (next to laundry)
	19 October 2013 SLR report:
Ceiling to side entrance to main house (next to laundry) - Chrysotile & Amosite Asbestos detected. Sample GF-F4-2. (Photo 275, 3m2).

	06/06/2024

	GF-F4-3
	Chrysotile Asbestos 
3 m2
	
Non-friable
	
Good condition
	Interior:
Ceiling to bathroom
 in residential flat
	19 October 2013 SLR report:
Ceiling to bathroom in residential flat - Chrysotile Asbestos detected. Sample GF-F4-3. (Photo 282, 3m2).

	06/06/2024

	GF-F5
	Chrysotile Asbestos 
> 5 m2
	
Non-friable
	
Good condition
	Exterior (ground level):
Shadow line profiled wall sheeting of the residence (elevation 1)
	19 October 2013 SLR report:
The Shadow line profiled wall sheeting to the external of the Residence - Chrysotile Asbestos fibre detected.

	06/06/2024

	GF-F6
	Chrysotile Asbestos 
> 5 m2
	
Non-friable
	
Good condition
	Exterior (ground level):
Shadow line profiled wall sheeting of the residence (elevation 2)
	19 October 2013 SLR report:
The Shadow line profiled wall sheeting to the external of the Residential Flat - Chrysotile Asbestos fibre detected.
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Date
	
Sample       No.
	Type of material identified or assumed and amount 
(Cross-sectional areas
 are estimates – measure before quoting)
	
Friable or non-friable asbestos
	

Condition of asbestos
	
Specific location of identified or assumed asbestos
	


Notes

	06/06/2024

	GF-F7
	Chrysotile Asbestos 
> 4 linear metres
	
Non-friable
	
Good condition
	Exterior (ground level):
Vent pipes to the building
	19 October 2013 SLR report:
Vent pipes to the building

	06/06/2024

	GF-F#
	Chrysotile & Amosite Asbestos 
15  m2
	
Eaves lining non-friable asbestos while remaining areas are low density board a friable asbestos
	
Good condition
	Exterior (ground level):
Ceiling to the covered walkway 

	19 October 2013 SLR report:
The ceiling to the covered walkway - Chrysotile & Amosite Asbestos fibre detected - LOW DENSITY BOARD. Sample GF-F?-1. (Photo 276, 15m2

	06/06/2024

	GF-F#-2
	Chrysotile Asbestos 
10  m2
	
Non-friable
	
Good Condition
	Exterior (ground and level 1):
Ceiling to the verandah and eaves 
	19 October 2013 SLR report:
The ceiling to the verandah and eaves - Chrysotile Asbestos fibre detected. Sample GF-F?-2. (Photo 277, 10m2).

	NON-ASBESTOS MATERIALS

The following materials were tested and found not to contain asbestos:


	Date 
	Sample 
No. 
	Result of Analysis
	Location 
	Notes

	06/06/2024

	GF-F4-1.
	19 October 2013 SLR report:
        No Asbestos fibre detected. Sample (Photo 269, 15m2).
	Interior:
Ceiling to bathroom/washroom in main house  
	Sampling found that the shower room ceiling does not contain asbestos. All other ceilings contain asbestos. Skylights in the main bathroom in Florence were found to contain asbestos.

	06/06/2024

	GF- F3-19
	19 October 2013 SLR report:
No Asbestos fibre detected (Photo 284, 2m2).
	Interior:
Side entrance to main house (next to laundry), 
south wall around window
	

	06/06/2024

	GF-F3-18
	19 October 2013 SLR report:
       No Asbestos fibre detected. (Photo 283, 0.25m2).
	Interior:
Side entrance to main house (next to laundry), 
east wall panel above door
	

	06/06/2024

	GF-F3-17
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 281, 2m2).
	Interior:
Residential flat bathroom, west wall (around bath)
	

	06/06/2024

	GF-F3-16
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 280, 4m2).
	Interior:
Residential flat bathroom, south wall (around sink) 
	

	06/06/2024

	GF-F3-15
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 279, 2m2).
	Interior:
Residential flat bathroom, east (around window) wall -
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	NON-ASBESTOS MATERIALS

The following materials were tested and found not to contain asbestos:


	Date 
	Sample 
No. 
	Result of Analysis
	Location 
	Notes

	06/06/2024

	GF-F3-14
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 278, 4m2).

	Interior:
Residential flat bathroom, north wall
	

	06/06/2024

	GF-F3-10
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 271, 6m2).
	Interior:
Lower east wall behind shower/toilets closest to hall
	

	06/06/2024

	GF- F3-7
	19 October 2013 SLR report:
       No Asbestos fibre detected. (Photo 268, 6m2).
	Interior:
Far west wall 
	

	06/06/2024

	GF-F3-6
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 267, 6m2).
	Interior:
South outer wall behind sink
	

	06/06/2024

	GF-F3-5
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 266, 5m2).
	Interior:
South inner wall
	

	06/06/2024

	GF-F3-4
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 265, 2m2).
	Interior:
North inner wall around window
	

	06/06/2024

	GF-F3-3
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 264, 4m2).
	Interior:
East wall at the end of the toilet cubicle
	

	06/06/2024

	GF-F3-2
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 263, 10m2).
	Interior:
Toilet partition walls 
	

	06/06/2024

	GF-F3-1
	19 October 2013 SLR report:
No Asbestos fibre detected. (Photo 262. 10m2).
	Interior:
North wall behind far shower
	[bookmark: _GoBack]Northern wall is low density board, which is located behind ceramic tiled shower recesses and a Tilux recess. These will have to be demolished to access northern wall.
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Photo 8 - asbestos vinyl tiles - laundry
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Photo 1 - south west elevation of house
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Photo 2 - southern elevation of flat adjacent to house
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